## Guy Calc Report
1. Calculations and guying specified at each location based on Final construction drawings.
2. Existing and proposed pole installations are determined based on POWER Engineers PLS-CADD Plan Drawing.
3. Guy label taken from PLS-CADD Pole Report provided by POWER Engineers.
4. Existing and proposed guy installations are determined based on POWER Engineers EST Map.
5. Guy Notes and Direction taken from POWER Engineers PLS-CADD EST Map.
6. Anchor Type specified by using Anchor Selection Guide in PacifiCorp standard EG041.
7. Usage % taken from 'Summary of Guy Usages - Maximum Usage %' in the PLS-CADD Pole Report provided by POWER Engineers.
8. Tension is calculated using Usage % multiplied by 'Cable Properties - Ultimate Tension' in the PLS-CADD Pole Report.
9. Total Max Anchor Tension is calculated by summing the guys attached to anchor, based on class 5 soil.
10. All new installations are assuming 7/16" UG guy wire installation
11. Red text indicates existing Transmission guying that is assumed to be 7/16" UG minimum.
12. Guys on same pole highlighted with the same color attach to the same anchor.
| Pole Number | Facility Pole ID | Existing or Proposed Pole | Guy Label | Type of Guy | Lead Length | Anchor Direction | Anchor Number | Anchor Type | % Usage | Guy Tension (lb) | Total Max Anchor Tension (lb) | Material to Include in RCMS Estimate
2030 | 01335006.0265101 | Proposed | PG11 | P1 to PG11 | -123.37662024 | 42.49361688 |  | EH121 ST50 |  | SW | 14.75
|  | Existing | NG12 | P1 to NG12 | -123.37662024 | 42.49361688 |  | EH121 ST50 |  | SW | 14.75
2040 | 01335006.0265102 | Proposed | PG11 | P1 to PG11 | -123.37553222 | 42.49382668 |  | EH131 ST50 |  | NE | 20.69
|  | Existing | NG12 | P1 to NG12 | -123.37553222 | 42.49382668 |  | EH131 ST50 |  | NE | 20.69
|  | Existing | CM21 | P1 to CM21 | -123.37556088 | 42.49382116 |  | EH131 ST50 |  | NE | 12.70
2080 | 01335006.0355901 | Proposed | P2 | P1 to P2 | -123.37691739 | 42.49050946 |  | EJ300 TAN | EH226 ST50 | SW | 40.85
|  | Existing | PG21 | P1 to PG21 | -123.37694458 | 42.49050902 |  | EJ300 TAN | EH226 ST50 | SW | 48.18
|  | Existing | CM22 | P1 to CM22 | -123.37694458 | 42.49050902 |  | EJ300 TAN | EH226 ST50 | SW | 48.18
|  | Existing | PG11 | P1 to PG11 | -123.37674220 | 42.49050607 |  | EJ300 TAN | EH226 ST50 | SE | 7.58
|  | Existing | CM12 | P1 to CM12 | -123.37674220 | 42.49050607 |  | EJ300 TAN | EH226 ST50 | SE | 7.58
2090 | 01335006.0354900 | Proposed | PG11 | P1 to PG11 | -123.37772589 | 42.49095341 |  | EH131 ST50 |  | NW | 16.14
|  | Existing | NG12 | P1 to NG12 | -123.37772589 | 42.49095341 |  | EH131 ST50 |  | NW | 16.14
|  | Existing | CM21 | P1 to CM21 | -123.37770798 | 42.49094526 |  | EH131 ST50 |  | NW | 10.47
2110 | 01335006.0356900 | Proposed | PG11 | P1 to PG11 | -123.37388568 | 42.49056845 |  | EH131 ST50 |  | E | 19.42
|  | Existing | NG12 | P1 to NG12 | -123.37388568 | 42.49056845 |  | EH131 ST50 |  | E | 19.42
|  | Existing | CM21 | P1 to CM21 | -123.37390436 | 42.49056808 |  | EH131 ST50 |  | E | 14.38
2140 | 01335006.0354801 | Proposed | PG11 | P1 to PG11 | -123.37699968 | 42.48953345 |  | EH201 ST50 |  | E | 27.50
|  | Existing | PG12 | P1 to PG12 | -123.37699968 | 42.48953345 |  | EH201 ST50 |  | E | 27.50
|  | Existing | CM21 | P1 to CM21 | -123.37701801 | 42.48953337 |  | EH201 ST50 |  | E | 22.55
2170 |  | Existing | PG11 | P1 to PG11 | -123.38060956 | 42.48953927 |  | EH121 ST50 |  | W | 31.35
|  | Existing | NG12 | P1 to NG12 | -123.38060956 | 42.48953927 |  | EH121 ST50 |  | W | 31.35
|  | Existing | CM21 | P1 to CM21 | -123.38057607 | 42.48953559 |  | EH121 ST50 |  | SW | 22.36
2180 | 01335006.0353801 | Proposed | PG11 | P1 to PG11 | -123.38050868 | 42.48952998 |  | EH111 ST50 |  | NE | 27.68
|  | Existing | NG12 | P1 to NG12 | -123.38050868 | 42.48952998 |  | EH111 ST50 |  | NE | 27.68
|  | Existing | CM21 | P1 to CM21 | -123.38051853 | 42.48951870 |  | EH111 ST50 |  | NE | 22.79
2190 | 01335006.0352800 | Proposed | PG11 | P1 to PG11 | -123.38128778 | 42.48863808 |  | EH131 ST50 |  | SW | 29.85
|  | Existing | NG12 | P1 to NG12 | -123.38128778 | 42.48863808 |  | EH131 ST50 |  | SW | 29.85
|  | Existing | CM21 | P1 to CM21 | -123.38127057 | 42.48865778 |  | EH131 ST50 |  | SW | 21.30
2220 | 01335006.0354702 | Proposed | PG11 | P1 to PG11 | -123.37696123 | 42.48816769 |  | EH111 ST50 |  | E | 23.49
|  | Existing | NG12 | P1 to NG12 | -123.37696123 | 42.48816769 |  | EH111 ST50 |  | E | 23.49
|  | Existing | CM21 | P1 to CM21 | -123.37697966 | 42.48816726 |  | EH111 ST50 |  | E | 18.52
2230 | 01335006.0354701 | Proposed | PG11 | P1 to PG11 | -123.37813641 | 42.48814042 |  | EH131 ST50 |  | W | 21.77
|  | Existing | NG12 | P1 to NG12 | -123.37813641 | 42.48814042 |  | EH131 ST50 |  | W | 21.77
2250 | 01335006.0355740 | Proposed | PG11 | P1 to PG11 | -123.37665644 | 42.48773226 |  | EH121 ST50 |  | W | 25.45
|  | Existing | NG12 | P1 to NG12 | -123.37665644 | 42.48773226 |  | EH121 ST50 |  | W | 25.45
2280 | 01335006.0357715 | Proposed | PG11 | P1 to PG11 | -123.37184404 | 42.48773756 |  | EH121 ST50 |  | E | 26.55
|  | Existing | NG12 | P1 to NG12 | -123.37184404 | 42.48773756 |  | EH121 ST50 |  | E | 26.55
|  | Existing | SE21 | P1 to SE21 | -123.37194283 | 42.48780704 |  | EH121 ST50 |  | N | 25.37
2285 | 01335006.0357704 | Proposed | PG11 | P1 to PG11 | -123.37193963 | 42.48712854 |  |  |  | S | 24.56
|  | Existing | SE12 | P1 to SE12 | -123.37193963 | 42.48712854 |  |  |  | S | 24.56
2290 | 01335006.0357800 | Proposed | PG11 | P1 to PG11 | -123.37193344 | 42.48882371 |  | EH121 | EH221 ST45 | N | 31.66
|  | Existing | NG12 | P1 to NG12 | -123.37193344 | 42.48882371 |  | EH121 | EH221 ST45 | N | 31.66
|  | Existing | PG21 | P1 to PG21 | -123.37187690 | 42.48873807 |  | EH121 | EH221 ST45 | E | 15.45
|  | Existing | NG22 | P1 to NG22 | -123.37187690 | 42.48873807 |  | EH121 | EH221 ST45 | E | 15.45
2300 | 01335006.0356800 | Proposed | PG11 | P1 to PG11 | -123.37297586 | 42.48871352 |  | EH131 ST45 |  | W | 17.61
|  | Existing | NG12 | P1 to NG12 | -123.37297586 | 42.48871352 |  | EH131 ST45 |  | W | 17.61
2310 | 01335006.0357801 | Proposed | PG11 | P1 to PG11 | -123.37185129 | 42.48885669 |  | EH121 ST45 |  | NW | 14.06
|  | Existing | NG12 | P1 to NG12 | -123.37185129 | 42.48885669 |  | EH121 ST45 |  | NW | 14.06
2320 | 01335006.0357802 | Proposed | PG11 | P1 to PG11 | -123.37092771 | 42.48882476 |  | EH101 | EH221 ST50 | SE | 16.97
|  | Existing | NG12 | P1 to NG12 | -123.37092771 | 42.48882476 |  | EH101 | EH221 ST50 | SE | 16.97
2330 |  | Existing | PG11 | P1 to PG11 | -123.37100237 | 42.48950886 |  | EH131 ST45 |  | N | 22.43
|  | Existing | NG12 | P1 to NG12 | -123.37100237 | 42.48950886 |  | EH131 ST45 |  | N | 22.43
2340 |  | Existing | PG11 | P1 to PG11 | -123.37097024 | 42.48825282 |  | EH131 ST45 |  | S | 15.16
|  | Existing | NG12 | P1 to NG12 | -123.37097024 | 42.48825282 |  | EH131 ST45 |  | S | 15.16
2360 | 01335006.0355603 | Proposed | PG11 | P1 to PG11 | -123.37653938 | 42.48646523 |  | EH111 ST50 |  | SW | 39.85
|  | Existing | NG12 | P1 to NG12 | -123.37653938 | 42.48646523 |  | EH111 ST50 |  | SW | 39.85
|  | Existing | CM21 | P1 to CM21 | -123.37641390 | 42.48648092 |  | EH111 ST50 |  | SW | 5.53
2370 | 01335006.0355600 | Proposed | CM11 | P1 to CM11 | -123.37492775 | 42.48666772 |  | EH101 ST50 |  | NE | 20.56
2380 | 01335006.0356600 | Proposed | PG11 | P1 to PG11 | -123.37351169 | 42.48683811 |  | EH131 ST50 |  | NE | 14.21
|  | Existing | NG12 | P1 to NG12 | -123.37351169 | 42.48683811 |  | EH131 ST50 |  | NE | 14.21
2390 | 01335006.0354601 | Proposed | PG11 | P1 to PG11 | -123.37703564 | 42.48648278 |  | EH111 ST50 |  | E | 18.74
|  | Existing | NG12 | P1 to NG12 | -123.37703564 | 42.48648278 |  | EH111 ST50 |  | E | 18.74
|  | Existing | CM21 | P1 to CM21 | -123.37706497 | 42.48648264 |  | EH111 ST50 |  | E | 10.83
2410 | 01335006.0353600 | Proposed | PG11 | P1 to PG11 | -123.37955189 | 42.48647131 |  | EH131 ST50 |  | W | 23.71
|  | Existing | NG12 | P1 to NG12 | -123.37955189 | 42.48647131 |  | EH131 ST50 |  | W | 23.71
|  | Existing | CM21 | P1 to CM21 | -123.37952189 | 42.48647144 |  | EH131 ST50 |  | W | 15.62
2430 | 01335006.0355501 | Proposed | PG11 | P1 to PG11 | -123.37655560 | 42.48547596 |  | EH111 ST50 |  | SW | 33.88
|  | Existing | NG12 | P1 to NG12 | -123.37655560 | 42.48547596 |  | EH111 ST50 |  | SW | 33.88
|  | Existing | CM21 | P1 to CM21 | -123.37652171 | 42.48547811 |  | EH111 ST50 |  | SW | 24.71
2440 | 01335006.0355602 | Proposed | PG11 | P1 to PG11 | -123.37540466 | 42.48556075 |  | EH111 ST50 |  | NW | 16.58
|  | Existing | NG12 | P1 to NG12 | -123.37540466 | 42.48556075 |  | EH111 ST50 |  | NW | 16.58
|  | Existing | PG21 | P1 to PG21 | -123.37522760 | 42.48554871 |  | EH111 ST50 |  | NE | 32.71
|  | Existing | NG22 | P1 to NG22 | -123.37522760 | 42.48554871 |  | EH111 ST50 |  | NE | 32.71
|  | Existing | CM31 | P1 to CM31 | -123.37525687 | 42.48554991 |  | EH111 ST50 |  | NE | 24.89
2450 | 01335006.0356500 | Proposed | PG11 | P1 to PG11 | -123.37434981 | 42.48520979 |  | EH131 ST50 |  | SE | 15.23
|  | Existing | NG12 | P1 to NG12 | -123.37434981 | 42.48520979 |  | EH131 ST50 |  | SE | 15.23
2470 | 01335006.0354502 | Proposed | PG11 | P1 to PG11 | -123.37666722 | 42.48403178 |  | EJ300 TAN | EH226 ST50 | SE | 22.46
|  | Existing | NG12 | P1 to NG12 | -123.37666722 | 42.48403178 |  | EJ300 TAN | EH226 ST50 | SE | 22.46
|  | Existing | CM21 | P1 to CM21 | -123.37669610 | 42.48403414 |  | EJ300 TAN | EH226 ST50 | SE | 14.63
2490 | 01335006.0353501 | Proposed | CM11 | P1 to CM11 | -123.37932305 | 42.48409540 |  | EH101 | EH221 ST50 | W | 18.17
2530 | 01335006.0352500 | Proposed | PG11 | P1 to PG11 | -123.38247774 | 42.48407651 |  | EH131 ST50 |  | W | 19.51
|  | Existing | NG12 | P1 to NG12 | -123.38247774 | 42.48407651 |  | EH131 ST50 |  | W | 19.51
|  | Existing | CM21 | P1 to CM21 | -123.38244755 | 42.48407669 |  | EH131 ST50 |  | W | 11.37
2540 | 01335006.0355500 | Proposed | PG11 | P1 to PG11 | -123.37646812 | 42.48403981 |  | EH201 ST50 |  | W | 15.45
|  | Existing | PG12 | P1 to PG12 | -123.37646812 | 42.48403981 |  | EH201 ST50 |  | W | 15.45
2590 | 01335006.0357402 | Proposed | PG11 | P1 to PG11 | -123.37181959 | 42.48388897 |  | EH111 ST50 |  | N | 26.62
|  | Existing | NG12 | P1 to NG12 | -123.37181959 | 42.48388897 |  | EH111 ST50 |  | N | 26.62
2600 | 01335006.0357401 | Proposed | PG11 | P1 to PG11 | -123.37182572 | 42.48325719 |  | EH131 ST50 |  | S | 21.75
|  | Existing | NG12 | P1 to NG12 | -123.37182572 | 42.48325719 |  | EH131 ST50 |  | S | 21.75
2630 | 01335006.0358504 | Proposed | PG11 | P1 to PG11 | -123.36940512 | 42.48405468 |  | EH121 ST50 |  | E | 13.95
|  | Existing | NG12 | P1 to NG12 | -123.36940512 | 42.48405468 |  | EH121 ST50 |  | E | 13.95
|  | Existing | PG21 | P1 to PG21 | -123.36946823 | 42.48397585 |  | EH121 ST50 |  | SW | 28.58
|  | Existing | NG22 | P1 to NG22 | -123.36946823 | 42.48397585 |  | EH121 ST50 |  | SW | 28.58
2645 | 01335006.0358501 | Proposed | PG11 | P1 to PG11 | -123.36958169 | 42.48470604 |  |  |  | NW | 8.06
|  | Existing | NG12 | P1 to NG12 | -123.36958169 | 42.48470604 |  |  |  | NW | 8.06
2650 | 01335006.0359500 | Proposed | PG11 | P1 to PG11 | -123.36811737 | 42.48432221 |  | EH131 ST50 |  | SE | 13.71
|  | Existing | NG12 | P1 to NG12 | -123.36811737 | 42.48432221 |  | EH131 ST50 |  | SE | 13.71
2660 | 01335006.0358500 | Proposed | PG11 | P1 to PG11 | -123.36935943 | 42.48509285 |  | EH131 ST55 |  | N | 13.41
|  | Existing | NG12 | P1 to NG12 | -123.36935943 | 42.48509285 |  | EH131 ST55 |  | N | 13.41
2670 | 01335006.0354402 | Proposed | PG11 | P1 to PG11 | -123.37670780 | 42.48337868 |  | EJ300 DDE | EH341 EH226 ST50 | NE | 13.35
|  | Existing | NG12 | P1 to NG12 | -123.37670780 | 42.48337868 |  | EJ300 DDE | EH341 EH226 ST50 | NE | 13.35
|  | Existing | PG21 | P1 to PG21 | -123.37674472 | 42.48328307 |  | EJ300 DDE | EH341 EH226 ST50 | S | 26.09
|  | Existing | PG22 | P1 to PG22 | -123.37674472 | 42.48328307 |  | EJ300 DDE | EH341 EH226 ST50 | S | 26.09
|  | Existing | PG31 | P1 to PG31 | -123.37674558 | 42.48340081 |  | EJ300 DDE | EH341 EH226 ST50 | N | 16.81
|  | Existing | PG32 | P1 to PG32 | -123.37674558 | 42.48340081 |  | EJ300 DDE | EH341 EH226 ST50 | N | 16.81
2680 | 01335006.0354401 | Proposed | PG11 | P1 to PG11 | -123.37717915 | 42.48307638 |  | EH131 ST45 |  | SW | 15.29
|  | Existing | NG12 | P1 to NG12 | -123.37717915 | 42.48307638 |  | EH131 ST45 |  | SW | 15.29
2700 | 01335006.0354302 | Proposed | SE11 | P1 to SE11 | -123.37670755 | 42.48177758 |  | EH101 ST55 |  | NE | 12.65
2730 | 01335006.0354203 | Proposed | P2 | P1 to P2 | -123.37690426 | 42.48044649 |  | EH101 | EH221 ST50 | W | 51.74
|  | Existing | PG11 | P1 to PG11 | -123.37697685 | 42.48044661 |  | EH101 | EH221 ST50 | W | 71.31
|  | Existing | PG12 | P1 to PG12 | -123.37697685 | 42.48044661 |  | EH101 | EH221 ST50 | W | 71.31
|  | Existing | PG13 | P1 to PG13 | -123.37697685 | 42.48044661 |  | EH101 | EH221 ST50 | W | 71.31
2750 | 01335006.0355203 | Proposed | PG11 | P1 to PG11 | -123.37488343 | 42.48044435 |  | EH131 ST50 |  | E | 30.44
|  | Existing | NG12 | P1 to NG12 | -123.37488343 | 42.48044435 |  | EH131 ST50 |  | E | 30.44
|  | Existing | CM21 | P1 to CM21 | -123.37491230 | 42.48044468 |  | EH131 ST50 |  | E | 22.65
2765 | 01335006.0354205 | Proposed | PG11 | P1 to PG11 | -123.37691952 | 42.48002067 |  |  |  | SW | 6.48
|  | Existing | NG12 | P1 to NG12 | -123.37691952 | 42.48002067 |  |  |  | SW | 6.48
|  | Existing | CM13 | P1 to CM13 | -123.37691952 | 42.48002067 |  |  |  | SW | 6.48
2770 | 01335006.0354207 | Proposed | PG11 | P1 to PG11 | -123.37669392 | 42.47989605 |  | EH121 ST50 |  | NW | 10.08
|  | Existing | CM13 | P1 to CM13 | -123.37669392 | 42.47989605 |  | EH121 ST50 |  | NW | 10.08
|  | Existing | NG12 | P1 to NG12 | -123.37669392 | 42.47989605 |  | EH121 ST50 |  | NW | 10.08
2780 | 01335006.0355100 | Proposed | PG11 | P1 to PG11 | -123.37591849 | 42.47972778 |  | EH131 ST55 |  | SE | 11.58
|  | Existing | NG12 | P1 to NG12 | -123.37591849 | 42.47972778 |  | EH131 ST55 |  | SE | 11.58
|  | Existing | CM21 | P1 to CM21 | -123.37593457 | 42.47973126 |  | EH131 ST55 |  | SE | 7.07
2790 | 01335006.0354104 | Proposed | P2 | P1 to P2 | -123.37683741 | 42.47939695 |  | EH106 | EH221 ST50 | SW | 46.27
|  | Existing | PG11 | P1 to PG11 | -123.37661562 | 42.47942578 |  | EH106 | EH221 ST50 | E | 14.73
|  | Existing | NG12 | P1 to NG12 | -123.37661562 | 42.47942578 |  | EH106 | EH221 ST50 | E | 14.73
|  | Existing | CM13 | P1 to CM13 | -123.37661562 | 42.47942578 |  | EH106 | EH221 ST50 | E | 14.73
|  | Existing | PG21 | P1 to PG21 | -123.37690204 | 42.47938590 |  | EH106 | EH221 ST50 | SW | 64.16
|  | Existing | PG22 | P1 to PG22 | -123.37690204 | 42.47938590 |  | EH106 | EH221 ST50 | SW | 64.16
|  | Existing | CM23 | P1 to CM23 | -123.37690204 | 42.47938590 |  | EH106 | EH221 ST50 | SW | 64.16
2810 | 01335006.0354101 | Proposed | PG11 | P1 to PG11 | -123.37893695 | 42.47940533 |  | EH121 ST50 |  | SW | 9.24
|  | Existing | NG12 | P1 to NG12 | -123.37893695 | 42.47940533 |  | EH121 ST50 |  | SW | 9.24
2820 | 01335006.0353100 | Proposed | PG11 | P1 to PG11 | -123.37947963 | 42.47996796 |  | EH131 ST45 |  | NW | 15.76
|  | Existing | NG12 | P1 to NG12 | -123.37947963 | 42.47996796 |  | EH131 ST45 |  | NW | 15.76
2840 | 01335006.0355102 | Proposed | PG11 | P1 to PG11 | -123.37626384 | 42.47860472 |  | EH101 | EH221 ST45 | NE | 13.54
|  | Existing | NG12 | P1 to NG12 | -123.37626384 | 42.47860472 |  | EH101 | EH221 ST45 | NE | 13.54
2850 | 01335006.0354105 | Proposed | PG11 | P1 to PG11 | -123.37700770 | 42.47846672 |  | EH131 ST45 |  | SW | 13.25
|  | Existing | NG12 | P1 to NG12 | -123.37700770 | 42.47846672 |  | EH131 ST45 |  | SW | 13.25
2870 | 01335006.0355002 | Proposed | PG11 | P1 to PG11 | -123.37567391 | 42.47722142 |  | EH106 ST50 |  | NE | 19.56
|  | Existing | NG12 | P1 to NG12 | -123.37567391 | 42.47722142 |  | EH106 ST50 |  | NE | 19.56
2880 | 01335006.0355004 | Proposed | P2 | P1 to P2 | -123.37569956 | 42.47669304 |  | EH121 ST50 |  | SE | 72.94
|  | Existing | PG11 | P1 to PG11 | -123.37569625 | 42.47665055 |  | EH121 ST50 |  | SE | 88.44
|  | Existing | PG12 | P1 to PG12 | -123.37569625 | 42.47665055 |  | EH121 ST50 |  | SE | 88.44
2890 | 01335006.0355003 | Proposed | PG11 | P1 to PG11 | -123.37553802 | 42.47685680 |  | EH111 ST50 |  | W | 31.34
|  | Existing | NG12 | P1 to NG12 | -123.37553802 | 42.47685680 |  | EH111 ST50 |  | W | 31.34
|  | Existing | CM21 | P1 to CM21 | -123.37550823 | 42.47685677 |  | EH111 ST50 |  | W | 23.30
2900 | 01335006.0356001 | Proposed | CM11 | P1 to CM11 | -123.37426810 | 42.47685863 |  | EH101 ST55 |  | NE | 12.61
2930 | 01335006.0357002 | Proposed | PG11 | P1 to PG11 | -123.37197636 | 42.47685913 |  | EH121 ST50 |  | E | 21.71
|  | Existing | NG12 | P1 to NG12 | -123.37197636 | 42.47685913 |  | EH121 ST50 |  | E | 21.71
|  | Existing | CM21 | P1 to CM21 | -123.37200662 | 42.47685892 |  | EH121 ST50 |  | E | 13.55
2940 | 01335006.0357001 | Proposed | PG11 | P1 to PG11 | -123.37194621 | 42.47687198 |  | EH121 ST50 |  | SW | 30.13
|  | Existing | NG12 | P1 to NG12 | -123.37194621 | 42.47687198 |  | EH121 ST50 |  | SW | 30.13
|  | Existing | CM21 | P1 to CM21 | -123.37192477 | 42.47689250 |  | EH121 ST50 |  | SW | 20.68
2950 | 01335006.0357000 | Proposed | CM11 | P1 to CM11 | -123.37117604 | 42.47760845 |  | EH101 ST55 |  | NE | 10.35
2960 | 01335006.0357101 | Proposed | PG11 | P1 to PG11 | -123.37052751 | 42.47832740 |  | EH131 ST55 |  | NE | 27.90
|  | Existing | NG12 | P1 to NG12 | -123.37052751 | 42.47832740 |  | EH131 ST55 |  | NE | 27.90